# Power Profile — Master Technical Documentation

Version: 1.0 · Date: 2026-07-01 · Author: Ahmed Zoher

Purpose: Master reference for graduation report and defense presentation.

All facts verified against actual source code with file:line citations.

Items that could not be confirmed in code are marked ⚠ NOT CONFIRMED IN CODE.

## Table of Contents

[Project Overview](#1-project-overview)

[Architecture and Technology Stack](#2-architecture-and-technology-stack)

[Database Schema](#3-database-schema)

[API Reference](#4-api-reference)

[Diversity Factors (IEC 60364-8-1)](#5-diversity-factors-iec-60364-8-1)

[Total Power Calculation](#6-total-power-calculation)

[Electrical Design Module (IEC 60364-5-52)](#7-electrical-design-module-iec-60364-5-52)

[Load Schedule and Energy Dispatch](#8-load-schedule-and-energy-dispatch)

[Solar Irradiance Model](#9-solar-irradiance-model)

[Battery and Storage Model](#10-battery-and-storage-model)

[Financial Analysis](#11-financial-analysis)

[Phase Balance Analysis](#12-phase-balance-analysis)

[Validation System and Automated Tests](#13-validation-system-and-automated-tests)

[Frontend Architecture](#14-frontend-architecture)

[Standards Referenced](#15-standards-referenced)

[Implemented vs Deferred Features](#16-implemented-vs-deferred-features)

## 1. Project Overview

Power Profile is a web-based electrical engineering design and energy management tool built as a graduation project. It targets building electrical designers, energy consultants, and project engineers working under Palestinian (PENRA) and IEC standards.

### Primary Capabilities

| Module | What It Computes |
| --- | --- |
| Total Power | Diversified apparent, active, and reactive power per room/floor/building/project with IEC 60364-8-1 diversity factors |
| Electrical Design | Full IEC 60364 panel schedules — circuit classification, breaker sizing, cable sizing (IEC 60364-5-52), phase assignment, voltage-drop per circuit |
| Load Schedule | 24-hour load profiles (max and optimized) × 7 days of week × any month; multi-source energy dispatch |
| Phase Balance | FFD greedy phase assignment, phasor neutral current, imbalance metric |
| Solar Irradiance | Location-aware hourly output using NASA POWER API with local PSH table fallback |
| Battery BESS | Multi-bank battery model; SOC tracking; runtime estimation |
| Financial Analysis | 25-year energy/cost projection; LCOE; generator fuel affine model; battery replacement scheduling |
| Validation | Live cross-check of all computed values against independently coded reference formulas; 36-test PHPUnit suite |

### System Context

Country target: Palestine (PENRA grid: 230 V / 400 V, 50 Hz)

Design ambient temperature: 40 °C (Palestinian summer design point)

Cable standard: IEC 60364-5-52 Table B.52.2, Method A1 (most conservative — conduit in thermally insulated wall), PVC/Cu

## 2. Architecture and Technology Stack

### Backend

| Layer | Technology | Notes |
| --- | --- | --- |
| Framework | Laravel 11 (PHP 8.2) | RESTful JSON API only |
| Auth | Laravel Sanctum + Google OAuth (Socialite) | Token-based; per-project role checks |
| ORM | Eloquent | No raw SQL in codebase (api.php comment, line 48) |
| Testing | PHPUnit 11 | 36 tests, 152 assertions |
| Rate limiting | Laravel throttle middleware | Heavy: 20/min; optimizer/financial: 10/min; general: per api-general config |
| External API | NASA POWER (GHI) | 30-day cache; ALLSKY_SFC_SW_DWN parameter |

### Frontend

| Layer | Technology |
| --- | --- |
| Framework | React 18 (Vite) |
| Routing | React Router v6 (lazy-loaded pages) |
| Styling | Tailwind CSS |
| HTTP client | Axios (frontend/src/api/axios.js) |
| Auth context | AuthContext with useAuth() hook |

### Directory Layout (key paths)

backend/

app/

Http/Controllers/Api/     — API controllers (one per domain)

Services/                 — Business logic, calculations, formulas

Models/                   — Eloquent models

database/migrations/        — 55 migration files (2026-03-26 → 2026-06-03)

routes/api.php              — All API route definitions

tests/Feature/              — PHPUnit feature tests

frontend/

src/

pages/                    — React page components (21 pages)

components/               — Reusable UI components

contexts/AuthContext.jsx  — Auth state management

api/axios.js              — Axios instance with base URL

App.jsx                   — Router with lazy-loaded pages

### Security Design (`backend/routes/api.php` lines 36–49)

Authentication: Sanctum token on every route

Authorization: $project->userRole($userId) on every project-scoped endpoint

SQL injection: Prevented by Eloquent ORM exclusively

CSRF: Active on web routes; API routes use Sanctum token

Data exposure: All responses scoped to the authenticated user's own projects

Roles: admin (project owner), main, normal, null (no access) — Project::userRole() at backend/app/Models/Project.php:66

## 3. Database Schema

### Entity Hierarchy

users

└── projects (user_id)

├── buildings (project_id)

│     ├── floors (building_id)

│     │     └── rooms (floor_id)

│     │           └── room_components (room_id, component_type_id)

│     ├── floor_components (floor_id)

│     └── building_components (building_id)

├── project_components (project_id)

├── utility_lines (morphMany lineable)

├── generator_lines (morphMany generable)

├── sockets (morphMany socketable)

├── batteries (project_id)

└── solar_systems (project_id)

Utility lines, generator lines, and sockets are polymorphic — they can be attached to any of: project, building, floor, or room.

### Key Tables and Columns

#### projects

| Column | Type | Notes |
| --- | --- | --- |
| id | bigint | PK |
| user_id | FK → users | Owner |
| name | string |  |
| building_type | string | Determines default DESIGN_RULES |
| currency_symbol | string |  |
| location_lat/lng | decimal | For solar calculations |
| location_name | string |  |
| work_days | json | Array of day names |
| work_time_intervals | json | Array of {start, end} |
| working_season_intervals | json |  |
| solar_source | string | 'max' or 'existing' |
| existing_solar_power | decimal | W |
| auto_backup_interval | integer |  |

Migration: 2026_03_26_142027_create_projects_table.php

#### room_components (representative — building/floor/project components share same schema)

| Column | Type | Notes |
| --- | --- | --- |
| room_id | FK → rooms |  |
| component_type_id | FK → component_types |  |
| power | decimal(10,2) | Apparent power in VA |
| phases | string | '1phase' or '3phase' |
| power_factor | decimal(4,2) | 0.01 – 1.00; default 1.00 |
| quantity | integer |  |
| priority | string(20) | 'normal', 'essential', 'critical' |
| needs_socket | boolean | → SOCKET circuit type |
| group_name | string | Group-max optimisation key |
| usage_time_intervals | json | Array of {start, end} |
| usage_season | string | 'all', 'summer', 'winter' |
| usage_day_type | string | 'all', 'weekday', 'weekend' |

Key migrations: 2026_04_20_120928, 2026_05_16_100000, 2026_04_27_300000, 2026_05_05_100000

#### batteries

| Column | Type | Notes |
| --- | --- | --- |
| project_id | FK |  |
| chemistry | string(50) | e.g., 'LiFePO4', 'lead_acid' |
| nominal_voltage_v | decimal |  |
| capacity_ah_per_unit | decimal |  |
| quantity | integer | Total cells/units |
| series_count | integer |  |
| parallel_count | integer |  |
| installation_date | date | For age calculation |
| depth_of_discharge | decimal(4,3) | e.g., 0.800 |
| round_trip_efficiency | decimal(4,3) | e.g., 0.950 |
| c_rate_charge | decimal(4,2) |  |
| c_rate_discharge | decimal(4,2) |  |
| rated_cycle_life | integer |  |
| current_soc | decimal(4,3) | Default 0.500 |
| is_active | boolean |  |

Migration: 2026_05_29_100000_create_batteries_table.php

#### utility_lines

| Column | Type |
| --- | --- |
| name, power (VA), phases |  |
| tariff_per_kwh, peak_tariff_per_kwh | float |
| peak_hours_start, peak_hours_end | integer (hour 0–23) |
| lineable_type, lineable_id | polymorphic |

#### generator_lines

| Column | Notes |
| --- | --- |
| power | VA |
| fuel_consumption_lph | Rated fuel consumption at 100% load (L/hr) |
| no_load_fuel_lph | Fuel at 0% load; defaults to 30% of rated if null |
| fuel_cost_per_liter | Currency/L |

#### solar_systems

| Column | Notes |
| --- | --- |
| capacity_kw | Named system capacity |
| is_active | boolean |
| installation_cost, annual_maintenance_cost | For LCOE |
| panel_lifetime_years |  |

## 4. API Reference

Base: all routes require Authorization: Bearer <sanctum-token> unless noted.

### Project Management

| Method | Endpoint | Controller Method |
| --- | --- | --- |
| GET | /api/projects | ProjectController@index |
| POST | /api/projects | ProjectController@store |
| GET | /api/projects/{project} | ProjectController@show |
| PUT | /api/projects/{project} | ProjectController@update |
| DELETE | /api/projects/{project} | ProjectController@destroy |
| GET | /api/projects/{project}/all-floors | allFloors |
| GET | /api/projects/{project}/all-rooms | allRooms |
| GET | /api/projects/{project}/shiftable-components | shiftableComponents |
| POST | /api/projects/{project}/optimize-shiftable | optimizeShiftable (throttle 10/min) |
| GET | /api/projects/{project}/defense-summary | defenseSummary |

### Hierarchy CRUD

Buildings → GET/POST /api/projects/{project}/buildings

Floors → GET/POST /api/buildings/{building}/floors

Rooms → GET/POST /api/floors/{floor}/rooms

Components → GET/POST /api/{rooms|floors|buildings|projects}/{id}/components

(Update/Delete pattern: PUT|DELETE /api/{type}-components/{id})

### Calculation Endpoints

| Endpoint | Throttle | Service |
| --- | --- | --- |
| GET /api/projects/{project}/total-power | api-heavy | TotalPowerController |
| GET /api/buildings/{building}/total-power | api-heavy | TotalPowerController |
| GET /api/floors/{floor}/total-power | api-heavy | TotalPowerController |
| GET /api/rooms/{room}/total-power | api-heavy | TotalPowerController |
| GET /api/projects/{project}/phase-balance | api-heavy | PhaseBalanceController |
| GET /api/projects/{project}/schedule | api-heavy | ScheduleController |
| GET /api/projects/{project}/load-profile | api-heavy | LoadProfileController |
| GET /api/projects/{project}/electrical-design | api-heavy | ElectricalDesignController |
| GET /api/projects/{project}/financial-analysis | 20/min | FinancialController |
| GET /api/projects/{project}/cost-signal | 30/min | CostSignalController |

### Polymorphic Resources (Utility Lines, Generator Lines, Sockets)

Each is available on 4 parent types: project, building, floor, room.

Example for utility lines:

GET /api/projects/{id}/utility-lines, POST /api/projects/{id}/utility-lines

PUT /api/utility-lines/{line}, DELETE /api/utility-lines/{line}

### Validation

| Endpoint | Notes |
| --- | --- |
| GET /api/validation/case-study | ValidationController@show — cross-checks all formula results |
| GET /api/validation/electrical-design | ValidationController@electricalDesign — verifies cable ampacity table |

### Admin (requires `admin` middleware)

GET /api/admin/users, PUT /api/admin/users/{user}, DELETE /api/admin/users/{user}

## 5. Diversity Factors (IEC 60364-8-1)

Service: backend/app/Services/DiversityFactorService.php

### Diversity Cascade

The system applies diversity factors at four levels:

Component  →  Room  →  Floor  →  Building  →  Project

(DF_room)  (room_to_floor)  (floor_to_building)  (DF_PROJECT = 0.70)

Critical-priority loads bypass all diversity factors (DF forced to 1.00).

Source: TotalPowerController.php line 192 — $effectiveDf = ($priority === 'critical') ? 1.0 : $resolvedDf

### Formula for Diversified Room Power

W_diversified = W_nameplate × DF_room × DF_room_to_floor × DF_floor_to_building × DF_PROJECT

Source: ScheduleController.php line 243:

$roomDf * $bDfs['room_to_floor'] * $bDfs['floor_to_building'] * self::DF_PROJECT

### Building-Type Diversity Factors (IEC 60364-8-1 / BS 7671 / CIBSE Guide C)

Source: DiversityFactorService.php lines 10–22

| Building Type | room_to_floor | floor_to_building |
| --- | --- | --- |
| residential_house | 0.60 | 0.70 |
| residential_apartment | 0.65 | 0.70 |
| hotel | 0.65 | 0.70 |
| office | 0.85 | 0.80 |
| educational_school | 0.80 | 0.80 |
| educational_university | 0.85 | 0.80 |
| retail | 0.85 | 0.85 |
| hospital | 0.90 | 0.90 |
| industrial | 0.85 | 0.85 |
| mosque_worship | 0.80 | 0.75 |
| sports | 0.80 | 0.80 |
| Default (unclassified) | 0.90 | 0.80 |

### Room Coincidence Factors (CIBSE / IEC usage demand factors)

Source: DiversityFactorService.php lines 28–50

| Room Type | DF |
| --- | --- |
| server_room | 1.00 |
| operating_theater | 1.00 |
| laboratory | 0.90 |
| classroom | 0.85 |
| lecture_hall | 0.85 |
| workshop | 0.85 |
| retail_floor | 0.85 |
| office_open | 0.80 |
| gym_sports | 0.80 |
| kitchen_commercial | 0.75 |
| office_private | 0.75 |
| prayer_hall | 0.75 |
| reception_lobby | 0.70 |
| meeting_room | 0.70 |
| corridor | 0.60 |
| living_room | 0.60 |
| kitchen_residential | 0.55 |
| hotel_room | 0.50 |
| bedroom | 0.45 |
| warehouse_storage | 0.30 |
| bathroom | 0.25 |
| Default | 0.80 |

### Project-Level DF

DF_PROJECT = 0.70 — applied at the building→project boundary.

Source: TotalPowerController.php line 22, ScheduleController.php line 19

## 6. Total Power Calculation

Controller: backend/app/Http/Controllers/Api/TotalPowerController.php

### Power Triangle

The power field in all component tables stores apparent power S in VA (nameplate value, already incorporating PF).

P (W) = S (VA) × PF

Q (VAR) = P × tan(arccos(PF))       [when PF < 1.0]

S_system = √(P_total² + Q_total²)

PF_system = P_total / S_system

Source: TotalPowerController.php line 181:

$w = $va * $pf;

$q = $pf < 1.0 ? $w * tan(acos(min(1.0, $pf))) : 0.0;

### System Constants

| Constant | Value | Source |
| --- | --- | --- |
| DF_PROJECT | 0.70 | TotalPowerController.php:22 |
| VOLTAGE_3PHASE_LL | 400 V | Line 25 |
| VOLTAGE_1PHASE | 230 V | Line 26 |
| SYSTEM_FREQUENCY | 50 Hz | Line 27 |
| TARGET_POWER_FACTOR | 0.95 | Line 28 |
| PF_CORRECTION_THRESHOLD | 0.85 | Line 29 |
| INRUSH_MULTIPLIER | 1.25 | Line 33 |

### Group-Max Optimisation

When group_name is set on a component, only the highest-VA component within that group is counted (group-max selection). This models mutual exclusivity of grouped loads (e.g., HVAC modes).

Source: TotalPowerController.php lines 196–208:

if (!$c->group_name) {

$vaTotal += $va; ...

} else {

$key = $c->{$entityKey} . '|' . $c->group_name;

if (!isset($groups[$key]) || $va > $groups[$key]['va']) {

$groups[$key] = ['va' => $va, 'w' => $wd, 'q' => $qd, ...];

}

}

### Continuous-load / Largest-Motor 125% (NEC 430.24/430.22)

The largest motor in the project is identified and its full-load VA is scaled at 125% per NEC 430.24/430.22 — the continuous-load sizing rule, which requires conductors and overcurrent devices to be rated at no less than 125% of the motor's full-load current. This is the continuous-load rule, not locked-rotor protection; locked-rotor inrush currents are 500–800% and are handled by the motor's separate overload relay or thermal protection device.

Inrush addition (VA) = motor_base_VA × (1.25 − 1.0) = motor_base_VA × 0.25

Source: TotalPowerController.php lines 88–111:

$delta = self::INRUSH_MULTIPLIER - 1.0;   // 0.25

$addVa = $motor['per_unit_va'] * $motor['quantity'] * $delta;

$addW  = $addVa * $motor['pf'];

$addQ  = $addVa * sqrt(max(0.0, 1.0 - $motor['pf'] ** 2));

### Power Factor Correction — Capacitor Bank

Correction is recommended when PF_system < 0.85. Target PF = 0.95.

Q_cap (kVAR) = P × (tan(arccos(PF_current)) − tan(arccos(PF_target)))

Capacitor configuration: Delta (Δ) connected to the 3-phase 400 V busbar.

C_phase (μF) = (Q_cap/3) / (2π × 50 × 400²) × 10⁶

Source: ValidationReferenceService.php:

$C_phase_μF = ($Q_cap/3) / (2 * M_PI * 50 * 400**2) * 1e6;

### Socket Demand (SocketDemandService)

Service: backend/app/Services/SocketDemandService.php

Socket outlet demand uses a tiered demand model:

First 10 outlets × 100%

Next 10 outlets × 75%

Remaining × 40%

200 VA per outlet

Coincidence factor by kVA band:

< 50 kVA → 1.00

50–250 kVA → 0.92

> 250 kVA → 0.85

### Backup Time Calculation

backup_hours (critical)  = usable_kwh / critical_kW

backup_hours (optimized) = available_kwh / optimized_kW

## 7. Electrical Design Module (IEC 60364-5-52)

Service: backend/app/Services/ElectricalDesignService.php

Controller: backend/app/Http/Controllers/Api/ElectricalDesignController.php

Frontend: frontend/src/pages/ElectricalDesignPage.jsx

Panel table component: frontend/src/components/PanelScheduleTable.jsx

### System Constants

Source: ElectricalDesignService.php lines 45–54

| Constant | Value | Standard |
| --- | --- | --- |
| V_PHASE | 230.0 V | PENRA / IEC |
| V_LINE | 400.0 V | PENRA / IEC |
| SQRT3 | 1.7320508 |  |
| AMBIENT_C | 40 °C | Palestinian design temp |
| DERATING_40C | 0.87 | IEC 60364-5-52 Table B.52.14: Cf = √((70−40)/(70−30)) = √0.75 ≈ 0.866 → tabled 0.87 |

### Cable Ampacity — IEC 60364-5-52 Table B.52.2, Method A1

Source: ElectricalDesignService.php lines 56–77

Table label: IEC 60364-5-52 Table B.52.2 — Method A1 (conductors in conduit in thermally insulated wall), PVC/Cu, 2 loaded conductors, 30 °C ambient reference. Adopted as the most conservative reference method to give a built-in safety margin.

| Size (mm²) | Iz at 30 °C (A) | Iz_derated at 40 °C (A) |
| --- | --- | --- |
| 1.5 | 14.5 | 12.6 |
| 2.5 | 19.5 | 17.0 |
| 4 | 26.0 | 22.6 |
| 6 | 34.0 | 29.6 |
| 10 | 46.0 | 40.0 |
| 16 | 61.0 | 53.1 |
| 25 | 80.0 | 69.6 |
| 35 | 99.0 | 86.1 |
| 50 | 119.0 | 103.5 |
| 70 | 151.0 | 131.4 |
| 95 | 182.0 | 158.3 |
| 120 | 210.0 | 182.7 |

Derated value = Iz × 0.87 — the actual design capacity used to select cable.

⚠ Note on 3-phase circuits: The code uses the 2-core column for all circuit types. For 3-phase HEAVY circuits the 3/4-core column would be ~8–11% lower; the 80% loading factor (breaker_loading_factor) partly compensates. No grouping derating (Table B.52.17) is applied. (ElectricalDesignService.php lines 59–62)

### Voltage-Drop Constants — mV/A/m

Source: ElectricalDesignService.php lines 79–98

Values for Cu 70°C PVC, Method A1, single-phase 2-conductor path. ⚠ Each marked for verification before licensed use.

| Size (mm²) | mV/A/m |
| --- | --- |
| 1.5 | 29.0 |
| 2.5 | 18.0 |
| 4 | 11.0 |
| 6 | 7.3 |
| 10 | 4.4 |
| 16 | 2.8 |
| 25 | 1.75 |
| 35 | 1.25 |
| 50 | 0.93 |
| 70 | 0.63 |
| 95 | 0.47 |
| 120 | 0.37 |

### Standard Breaker Sizes (IEC 60898 / IEC 60947-2)

Source: ElectricalDesignService.php line 101:

[6, 10, 16, 20, 25, 32, 40, 50, 63, 80, 100, 125, 160, 200, 250, 315, 400]

### Circuit Classification (5 Types)

Source: ElectricalDesignService.php lines 525–553

Classification precedence (evaluated in order):

HEAVY — if: 3-phase OR VA ≥ heavy_threshold_va OR (is_motor AND VA ≥ motor_dedicated_threshold_va)

CRITICAL — if: priority === 'critical'

SOCKET — if: needs_socket === true

LIGHTING — if: component type name matches luminaire keywords (light, lamp, led strip, chandelier, luminaire, lantern, sconce, bulb, pendant, downlight, spotlight, fluorescent, fixture)

AUXILIARY — all remaining (small motors, fans, speakers, sensors, PoE)

Luminaire preset names: Light, Fluorescent Lamp, LED Strip, Chandelier (ElectricalDesignService.php lines 114–122)

### Design Rules by Building Type

Source: ElectricalDesignService.php lines 124–247

| Parameter | hospital | data_center | office | residential | school | mosque | mall | default |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| heavy_threshold_va | 1500 | 1000 | 2000 | 2000 | 2000 | 2000 | 3000 | 2000 |
| motor_dedicated_va | 750 | 500 | 750 | 750 | 750 | 750 | 1000 | 750 |
| socket_outlets/circuit | 6 | 4 | 8 | 8 | 8 | 8 | 8 | 8 |
| lighting_breaker_a | 10 | 10 | 10 | 10 | 10 | 10 | 16 | 10 |
| socket_breaker_a | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |
| auxiliary_breaker_a | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |
| breaker_loading_factor | 0.80 | 0.70 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 |
| spare_capacity_pct | 20% | 30% | 10% | 10% | 15% | 10% | 15% | 10% |
| rcd_policy | 30mA_all | 30mA_socket_lighting | 30mA_sl | 30mA_sl | 30mA_sl | 30mA_sl | 30mA_sl | 30mA_sl |
| essential_separation | true | true | false | false | false | false | false | false |
| standard_ref | IEC+HTM06 | IEC+EN50600 | IEC 60364 | IEC 60364 | IEC 60364 | IEC 60364 | IEC 60364 | IEC 60364 |

### Design Current Formulas

Source: ElectricalDesignService.php lines 862–868

1-phase:  Ib = S_VA / V_phase = S_VA / 230   [A]

3-phase:  Ib = S_VA / (√3 × V_line) = S_VA / (√3 × 400)   [A]

Critical design note: The breaker and cable carry the full apparent current (S÷V), not the active component (P÷V). PF is NOT applied to Ib. (ElectricalDesignService.php header comment lines 22–26)

### Cable Selection Algorithm

Source: ElectricalDesignService.php lines 832–900

Step 1: Compute Ib (design current, from VA and phase)

Step 2: Select minimum breaker In ≥ max(type_min_breaker, next_standard_size(Ib))

Step 3: Select minimum cable where Iz_table × 0.87 ≥ In

Step 4: Apply type minimum: 1.5 mm² for LIGHTING/AUXILIARY; 2.5 mm² for SOCKET/MIXED

Step 5: PE = cable (≤16 mm²), PE = 16 mm² (16–35 mm²), PE = cable/2 (>35 mm²)

Step 6: Breaker curve: LIGHTING→B, motor→D, all others→C

PE sizing rule (IEC 60364-5-54 3-band rule), ElectricalDesignService.php lines 895–900:

if ($s <= 16.0) return $s;

if ($s <= 35.0) return 16.0;

return $s / 2.0;

### Voltage Drop Calculation

Source: ElectricalDesignService.php lines 939–974

ΔU (V) = (mV/A/m) × Ib × length_m / 1000

ΔU (%) = ΔU / V_nominal × 100

V_nominal: 230 (1-phase) or 400 (3-phase)

Limits (IEC 60364-8-1 Table 1):

LIGHTING circuits: 3%

All other types: 5%

When ΔU% > limit, the service computes vd_remedy_cable_mm2 — the smallest larger cable that keeps VD within the limit.

When length_m is not provided (null), vd_note: 'length required' is returned and VD is not computed.

Worked example:

Circuit: SOCKET, 1-phase, 6 A breaker, 2.5 mm² cable, Ib = 5.0 A, length = 20 m

ΔU (V) = 18.0 × 5.0 × 20 / 1000 = 1.80 V

ΔU (%) = 1.80 / 230 × 100 = 0.78% → within 5% limit

### Circuit Packing Strategy

SOCKET circuits (packSocketCircuits, lines 593–635):

Accumulate loads until VA limit OR outlet count limit is exceeded

VA limit = socket_breaker_a × V_PHASE × breaker_loading_factor

Outlet limit = socket_outlets_per_circuit

LIGHTING circuits (packLightingLoads, lines 637–679):

Cross-room packing (lighting from multiple rooms shares one circuit)

VA limit = lighting_breaker_a × V_PHASE × breaker_loading_factor

Force-close at floor midpoint to guarantee ≥2 lighting circuits per floor

AUXILIARY circuits (packAuxiliaryLoads, lines 681–723):

Cross-room packing (like lighting)

VA limit = auxiliary_breaker_a × V_PHASE × breaker_loading_factor

Never mixed with lighting or sockets

HEAVY and CRITICAL (buildSingleLoadCircuit, lines 557–591):

Always dedicated one-per-load circuits

### group_small_critical Option

Source: ElectricalDesignService.php lines 355, 387–395, 449–463

When group_small_critical = true (set per building type), critical loads with va_each < motor_dedicated_threshold_va (default 750 VA) are collected across the floor and packed into a single shared CRITICAL circuit, rather than each getting a dedicated breaker. This reduces panel space for buildings with many small life-safety sensors/devices. The default is false for all currently-defined building types.

### Dedicated Rooms

Source: ElectricalDesignService.php lines 103–112

These room types get dedicated SOCKET circuits (sockets not shared across rooms):

kitchen_residential, kitchen_commercial, bathroom, laboratory, workshop, server_room, operating_theater

Keyword-based detection also catches rooms named with: kitchen, bathroom, lab, workshop, server, critical, operating

Lighting from dedicated rooms still joins the normal floor lighting pool.

### Panel Hierarchy Output

The API returns a tree structure:

project

└── buildings[]

├── mdb          (Main Distribution Board)

│    ├── incomer (current, breaker, cable, PE)

│    ├── phase_balance_va (A/B/C in VA)

│    └── phase_imbalance_pct

├── mdb_circuits[] (floor feeders + building-direct)

├── essential_panel (if essential_separation=true)

└── floors[]

├── db (incomer, phase balance)

└── circuits[] (per circuit: type, VA, Ib, In, curve, cable, PE, RCD, VD data)

### Phase Assignment in Electrical Design

Source: ElectricalDesignService.php — assignPhases() method.

Uses the same FFD greedy algorithm as PhaseBalanceController: sort circuits by VA descending, assign each to the least-loaded phase.

### MDB Incomer Sizing

MDB_incomer_VA = building_diversified_VA × (1 + spare_capacity_pct/100)

Floor_DB_incomer_VA = floor_diversified_VA × (1 + spare_capacity_pct/100)

Building diversified VA:

building_div_VA = Σ(floor_div_VA) × floor_to_building + building_own_VA

floor_div_VA = Σ(room_VA × room_DF × room_to_floor) + floor_own_VA

Source: ElectricalDesignService.php lines 300–308, 478–479

## 8. Load Schedule and Energy Dispatch

Controller: backend/app/Http/Controllers/Api/ScheduleController.php

Service: backend/app/Services/SourceDispatchService.php

### Schedule Endpoint Behavior

GET /api/projects/{project}/schedule?month=1–12&day=1–31

Returns load profiles for all 7 days of the week computed in a single request:

load_max — all components on, no diversity applied

load_optimized — group-max selection applied + diversity factors

hourly_kvar — reactive power profile

dispatch_max — source dispatch for max load

dispatch_optimized — source dispatch for optimized load

Solar profile uses performanceRatio: 0.80 for hourly output (ScheduleController.php line 82).

### Solar Capacity Modes

Source: ScheduleController.php lines 63–75

solar_source = 'max' — uses roof area estimate: SolarIrradianceService::estimateCapacityW(totalAreaM2)

solar_source = 'existing' — uses sum of active solar_systems.capacity_kw × 1000; falls back to existing_solar_power fields if no named systems exist

### Source Capacities

utility_capacity_W = Σ(utility_lines.power) × 0.8    [VA → W at PF=0.8]

generator_capacity_W = Σ(generator_lines.power) × 0.8

Source: ScheduleController.php lines 90–93

### 7-Step Energy Dispatch Algorithm

Service: backend/app/Services/SourceDispatchService.php

For each hour of the day, the dispatch service allocates supply from sources in this priority order:

Solar direct use — serve load from available solar generation

Solar → paired battery charge — excess solar charges batteries paired to that solar system

Solar → shared solar pool — remaining solar to shared battery banks

Unpaired battery charge (from solar)

Battery discharge — discharge batteries to serve remaining load

Utility grid — draw from utility for remaining load (up to utilCapW)

Generator — last resort; operates within ISO_OPTIMAL_MAX_LOAD = 0.85

Constants:

GEN_OPTIMAL_MAX_LOAD = 0.85 (ISO 8528 optimal band ceiling)

INV_EFF = 0.95 (inverter efficiency applied to battery round-trips)

### Battery Round-Trip Efficiency in Dispatch

charge:    SOC += (chargeW / 1000) × √(round_trip_efficiency)

discharge: SOC -= (dischargeW / 1000) / √(round_trip_efficiency)

One-way efficiency = √(RTE) applied on both charge and discharge legs.

Source: SourceDispatchService.php

### Load Profile Diversity in Schedule

Source: ScheduleController.php lines 230–243

Diversity cascade for schedule is identical to total power cascade:

room_load × room_DF × room_to_floor × floor_to_building × DF_PROJECT(0.70)

Critical loads always use effectiveDf = 1.0 (ScheduleController.php line 296).

### Shiftable Load Optimisation

POST /api/projects/{project}/optimize-shiftable

Moves shiftable loads (flagged in component table) to off-peak hours to minimize cost. Uses CostSignalService tariff schedule.

Rate limited to 10 requests/minute.

## 9. Solar Irradiance Model

Service: backend/app/Services/SolarIrradianceService.php

### Solar Capacity Estimate

Source: SolarIrradianceService.php

estimateCapacityW = building_area_m² × ROOF_COVERAGE_RATIO × STC_IRRADIANCE × CAPACITY_ESTIMATE_PR

= area × 0.17 × 1000 × 0.75

Constants:

ROOF_COVERAGE_RATIO = 0.17 (17% of roof area usable for panels)

STC_IRRADIANCE = 1000 W/m²

CAPACITY_ESTIMATE_PR = 0.75

⚠ Heuristic note: This formula is a rough upper-bound estimate only. ROOF_COVERAGE_RATIO = 0.17 is the fraction of roof area physically usable for panels; CAPACITY_ESTIMATE_PR = 0.75 accounts for cable, inverter, and mismatch losses. Module conversion efficiency (~0.19 for typical crystalline silicon) is not embedded in either constant — the formula does not model panel-level efficiency and therefore overestimates actual AC output. For engineering-grade calculations use the explicit form: P_ac = area × coverage_ratio × G_stc × η_module × PR (e.g., area × 0.17 × 1000 × 0.19 × 0.75).

### Solar Declination

The declination formula used is Cooper (1969):

δ (°) = 23.45 × sin(360/365 × (DOY − 81))

where DOY = day of year.

Source: SolarIrradianceService.php

### Sunrise/Sunset

cos(H_ss) = −tan(latitude) × tan(δ)

H_ss = solar hour angle at sunset (degrees)

daylight_hours = 2 × H_ss / 15

### Hourly Output Profile

peak_output_W = capacity_kW × 1000 × PSH × PR × π / (2 × daylight_hours)

Performance ratio for hourly profile: PR = 0.80 (ScheduleController.php line 82).

### PSH Lookup Table

7 latitude bands (0°–60°) × 12 months stored as a table in the service. When location is known, the service first checks the NASA POWER API cache; falls back to PSH table if API unavailable.

### NASA POWER API Integration

Parameter: ALLSKY_SFC_SW_DWN (all-sky surface shortwave downwelling irradiance, GHI in W/m²)

Hardcoded year: 2023

Cache: 30 days

Fallback: PSH lookup table

## 10. Battery and Storage Model

Model: backend/app/Models/Battery.php

Controller: backend/app/Http/Controllers/Api/BatteryController.php

### Capacity Calculations

Source: Battery.php model attributes

nominal_capacity_kwh = nominal_voltage_V × capacity_ah_per_unit × quantity / 1000

### Age Degradation

age_factor = max(0.70, 1 − age_years × degradation_per_year)

usable_capacity_kwh = nominal_capacity_kwh × depth_of_discharge × age_factor

Battery health thresholds:

≥ 0.90 → Good

≥ 0.80 → Fair

≥ 0.70 → Degraded

< 0.70 → Replace

### Charge/Discharge Power Limits

max_charge_power_kW  = nominal_capacity_kwh × c_rate_charge

max_discharge_power_kW = nominal_capacity_kwh × c_rate_discharge

### Runtime Estimation

GET /api/projects/{project}/battery-runtime

runtime_hours = usable_kwh / load_kW

POST /api/batteries/{battery}/runtime-at-load — computes runtime at a specified load.

### Battery Replacement Projection

Source: FinancialAnalysisService.php

replacement_year = ceil((rated_cycle_life / 365) − age_years)

## 11. Financial Analysis

Service: backend/app/Services/FinancialAnalysisService.php

Controller: backend/app/Http/Controllers/Api/FinancialController.php

### Key Constants

Source: FinancialAnalysisService.php

| Constant | Value |
| --- | --- |
| PANEL_DEGRADATION | 0.005 (0.5%/year) |
| PROJECTION_YEARS | 25 |
| DF_PROJECT | 0.70 |

### Generator Fuel Model (Affine)

Model: backend/app/Models/GeneratorLine.php

F(P) = F₀ + (F_rated − F₀) × P / P_rated     [L/hr]

where:

F_rated = fuel_consumption_lph (at rated power P_rated)

F₀ = no_load_fuel_lph (default = 0.30 × F_rated if not set)

P = actual output power [kW]

This is an affine (linear two-point) model: fuel consumption is nonzero at zero load, increases linearly to rated.

Cost at rated load:

cost_per_kwh = fuel_cost_per_liter × fuel_consumption_lph / rated_power_kW

Marginal cost (incremental, used by CostSignalService):

marginal_cost_per_kwh = fuel_price × (F_rated − F₀) / P_rated

Source: GeneratorLine.php

### Weighted Tariff

weighted_tariff = (offPeakHours × tariff + peakHours × peakTariff) / 24

### 25-Year Energy Projection

annual_solar_kwh_year_n = solar_kwh_base × (1 − 0.005)^n    [panel degradation]

year_net = annual_savings × (0.995)^year − battery_replacement_cost_if_applicable

### LCOE (Simple / Undiscounted)

LCOE = (solar_install_cost + annual_maintenance_cost × 25) / (solar_kwh_annual × 25)

Note: This is the simple (undiscounted) LCOE. No NPV, IRR, or time-value-of-money adjustment is applied. Source: FinancialAnalysisService.php

### Generator Oversizing Warning

Source: FinancialAnalysisService.php

If average generator loading < 30%, a warning is issued.

Recommended size: peak_load / 0.75 (targeting 75% average loading per ISO 8528).

## 12. Phase Balance Analysis

Controller: backend/app/Http/Controllers/Api/PhaseBalanceController.php

### Constants

Source: PhaseBalanceController.php

| Constant | Value |
| --- | --- |
| VOLT | 230 V |
| WARN_PCT | 10% |
| CRIT_PCT | 20% |
| SOCKET_ASSUMED_PF | 0.95 |

Phase voltage angles: A = 0°, B = 120°, C = 240°

### Phasor Current Calculation

For each load on phase P with power factor PF:

θ_V = phase voltage angle (0° / 120° / 240°)

θ_I = θ_V − arccos(PF)    [current lags voltage by arccos(PF)]

I_re += |I| × cos(θ_I)

I_im += |I| × sin(θ_I)

Source: PhaseBalanceController.php

### Neutral Current

Phasor (complex) sum of the three phase currents:

I_N = √((I_A_re + I_B_re + I_C_re)² + (I_A_im + I_B_im + I_C_im)²)

For a perfectly balanced 3-phase system, I_N → 0.

### Imbalance Metric

imbalance_pct = (I_max − I_min) / I_avg × 100

where I_max, I_min, I_avg are the magnitudes of currents on phases A, B, C.

Note: This is a spread metric (max-min range / mean), not the standard NEMA MG-1 voltage imbalance definition (which uses deviations from average). Source: PhaseBalanceController.php

Thresholds: WARN at 10%, CRITICAL at 20%.

### FFD Greedy Phase Assignment

Used in both ElectricalDesignService and PhaseBalanceController:

Sort all load blocks by VA (descending — largest first)

For each block: assign to the currently least-loaded phase

Repeat until all loads assigned

Effect: Near-optimal phase balancing with O(n log n) complexity (sort dominates).

## 13. Validation System and Automated Tests

### PHPUnit Test Suite

File: backend/tests/Feature/ElectricalDesignTest.php

Status: 36 tests, 152 assertions — all passing.

Test coverage includes:

Cable ampacity table verification: for each of the 12 sizes, asserts the value matches IEC 60364-5-52 Table B.52.2, Method A1

Derating factor at 40°C: 0.87

Voltage drop spot checks (2 known cases)

The tests use PHP reflection to access the private CABLE_AMPACITY constant directly.

Test docblock: Table B.52.2, Method A1 (conduit in thermally insulated wall), 2 loaded conductors

### Validation API (Cross-Check Service)

Controller: backend/app/Http/Controllers/Api/ValidationController.php

`GET /api/validation/case-study` — Runs a complete independent recalculation of:

Room-level diversity cascade

Floor-level diversity cascade

Building-level diversity

Project diversity (0.70 × above)

Capacitor bank sizing

Motor inrush

Uses ValidationReferenceService.php — an independent PHP implementation of all formulas that does NOT call the main services. Cross-checks the main API output and returns overall_status: PASS | FAIL with per-check results.

`GET /api/validation/electrical-design` — Uses PHP reflection to read the live CABLE_AMPACITY constant from ElectricalDesignService, runs 12 ampacity checks + derating check + 2 VD spot checks. Returns overall_status: PASS | FAIL.

### Validation UI

Page: frontend/src/pages/ValidationPage.jsx

Two sections:

Case Study Comparison Table — formula cross-check results with reference vs. computed values

Electrical Design Validation — cable ampacity table with IEC reference, derating row, 2 VD spot checks

Card sub-header for electrical design section:

"IEC 60364-5-52 Table B.52.2 · Method A1 (thermally insulated wall) · Cu 70°C PVC · 30°C ambient · most conservative"

## 14. Frontend Architecture

Entry point: frontend/src/App.jsx

### Routing Structure

All project-internal pages use <ProjectLayout> as a nested route wrapper (provides sidebar navigation).

| Route | Page | Notes |
| --- | --- | --- |
| / | → redirect to /dashboard |  |
| /login | LoginPage | Public only |
| /auth/callback | AuthCallbackPage | Google OAuth callback |
| /dashboard | DashboardPage | Protected |
| /validation | ValidationPage | Protected, no project context |
| /defense-prep | DefensePrepPage | Protected |
| /projects/:projectId | ProjectPage | ProjectLayout |
| /projects/:projectId/buildings/:buildingId | BuildingPage | ProjectLayout |
| /projects/:projectId/buildings/:buildingId/floors/:floorId | FloorPage | ProjectLayout |
| .../rooms/:roomId | NewRoomPage | ProjectLayout |
| /projects/:projectId/schedule | LoadSchedulePage | ProjectLayout |
| /projects/:projectId/phase-balance | PhaseBalancePage | ProjectLayout |
| /projects/:projectId/financial | FinancialPage | ProjectLayout |
| /projects/:projectId/single-line | SingleLineDiagramPage | ProjectLayout |
| /projects/:projectId/electrical-design | ElectricalDesignPage | ProjectLayout |

All pages use lazy() loading (code-splitting).

### Key Components

| Component | Purpose |
| --- | --- |
| PanelScheduleTable.jsx | Renders the per-panel circuit schedule table with inline VD input |
| ProjectSidebar.jsx | Left-side navigation within a project |
| LoadingSpinner.jsx | Suspense fallback |
| ErrorBoundary.jsx | Per-route error isolation |

### Auth Flow

User logs in via /login (email/password or Google OAuth)

Backend returns Sanctum token

Token stored; AuthContext provides user and isLoading to all children

ProtectedRoute wraps all authenticated pages; unauthenticated → redirect /login

PublicRoute wraps login page; authenticated → redirect /dashboard

### Data Fetching Pattern

All pages use useEffect + Axios:

api.get(`/api/projects/${projectId}/electrical-design`)

.then(res => setData(res.data))

.catch(err => setError(err.response?.data?.message ?? 'Failed to load'))

.finally(() => setLoading(false));

### Electrical Design UI — Key Behaviors

Building section (ElectricalDesignPage.jsx:BuildingSection): collapsible floors, MDB summary stat cards

Stat cards: Nameplate Total (kVA), Diversified Demand (kVA + % of nameplate), MDB Incomer (A + cable mm²), Phase Imbalance (% — red/amber/green)

Engineering notice (ElectricalDesignPage.jsx:250–256): states Table B.52.2, Method A1, most conservative; instructs user to enter cable lengths for VD

vdTable passed to PanelScheduleTable for client-side VD remedy lookup

## 15. Standards Referenced

| Standard | Application in System |
| --- | --- |
| IEC 60364-5-52 | Cable ampacity (Table B.52.2, Method A1), VD limits (Table 1), install method A1, derating factors (Table B.52.14) |
| IEC 60364-5-54 | PE conductor sizing (3-band rule: ≤16 mm² → equal; 16–35 mm² → 16 mm²; >35 mm² → half) |
| IEC 60364-8-1 | Diversity factors at all levels; building-type DFs; room coincidence factors |
| IEC 60898 | Standard MCB ratings (B/C/D curve trip classes) |
| IEC 60947-2 | MCB/MCCB rating standard (noted in code as breaker standard) |
| NEC Article 430 / IEC | Motor inrush 125% sizing factor |
| ISO 8528 | Generator optimal load band (70–85%); oversizing warning at <30% average load |
| PENRA | Palestinian Energy and Natural Resources Authority: 230 V / 400 V, 50 Hz system; PF target 0.95; correction threshold 0.85 |
| CIBSE Guide C / BS 7671 | Room coincidence factors and building-type diversity factors |
| NASA POWER | GHI data (ALLSKY_SFC_SW_DWN) for solar irradiance calculations |

Note on IEC 60364-5-52 mV/A/m values: All voltage-drop mV/A/m values in CABLE_VD_MV_A_M are individually marked ⚠ VERIFY in the source code (ElectricalDesignService.php lines 86–97). They are engineering estimates derived from IEC 60364-5-52 / BS 7671 Appendix 4 Table 4D2B and should be verified against the current standard edition before a licensed submission.

## 16. Implemented vs Deferred Features

### Fully Implemented

| Feature | Evidence |
| --- | --- |
| IEC 60364-8-1 diversity factors (11 building types, 20 room types) | DiversityFactorService.php |
| Socket demand tiered model (200 VA/outlet, first 10 × 100%, next 10 × 75%, rest × 40%) | SocketDemandService.php |
| Reactive power and capacitor bank sizing (delta Δ, PF 0.85→0.95) | TotalPowerController.php |
| Motor inrush 125% (NEC/IEC) | TotalPowerController.php:33 |
| Electrical design panel schedules (5 circuit types, all building types) | ElectricalDesignService.php |
| Cable sizing IEC 60364-5-52 Table B.52.2 Method A1 | ElectricalDesignService.php:64–77 |
| Voltage drop per circuit (mV/A/m method) with remedy suggestion | ElectricalDesignService.php:948–974 |
| PE sizing (IEC 60364-5-54 3-band rule) | ElectricalDesignService.php:895–900 |
| Breaker curve selection (B/C/D) | ElectricalDesignService.php:878–883 |
| Phase assignment FFD greedy + phasor neutral current | PhaseBalanceController.php |
| 7-step multi-source energy dispatch with battery SOC tracking | SourceDispatchService.php |
| Solar irradiance (NASA POWER API + PSH table fallback) | SolarIrradianceService.php |
| Affine generator fuel model | GeneratorLine.php |
| LCOE (simple/undiscounted, 25-year) | FinancialAnalysisService.php |
| Battery degradation and replacement scheduling | Battery.php, FinancialAnalysisService.php |
| Generator oversizing detection (<30% average load) | FinancialAnalysisService.php |
| Essential panel separation (hospital, data center) | ElectricalDesignService.php:312 |
| group_small_critical packing option | ElectricalDesignService.php:355 |
| PHPUnit test suite (36 tests, 152 assertions) | ElectricalDesignTest.php |
| Live validation API with reference implementation | ValidationController.php, ValidationReferenceService.php |
| Project backup/restore (JSON), building/floor/room scoped | ProjectBackupController.php |
| Multi-user project collaboration (roles: admin/main/normal) | ProjectMemberController.php |
| Google OAuth login | AuthController.php via Socialite |
| Admin panel (user management) | AdminController.php |
| Named solar systems (multiple per project) | SolarSystem model, SolarSystemController.php |
| Multi-battery bank model | Battery model, BatteryController.php |

### Known Limitations (Current Implementation)

Protection coordination and short-circuit calculation — MCB ratings are selected from standard IEC 60898 sizes but short-circuit current levels and cascading coordination are not calculated

Grouping derating (Table B.52.17) — no derating for multiple circuits in the same conduit

3-phase cable column vs 2-core column — 3-phase HEAVY circuits use the 2-core ampacity column (conservative but not strictly correct); the 3/4-core column is ~8–11% lower

mV/A/m values — engineering estimates; each marked ⚠ VERIFY in code

Module efficiency — not explicitly applied as a separate factor in solar capacity estimate

LCOE — simple/undiscounted; no NPV or IRR

Cooper declination formula — code comments say "Spencer"; the formula implemented is Cooper (1969)

NASA POWER year — hardcoded to 2023

### Deferred / Not Implemented

Short-circuit calculation and fault current analysis

Protection coordination study (upstream/downstream selectivity)

Harmonic distortion analysis (THD)

Arc flash hazard study

Earthing (grounding) system design

Load flow simulation for distribution network

Mobile application

*Document generated from source code reading on 2026-07-01. All formulas and constants verified against file:line citations listed. Items marked ⚠ require independent verification before licensed engineering submission.*

## Section 17 — Page-by-Page User Walkthrough

This section documents every page the user encounters, in natural workflow order. For each page: its purpose, every input field (what it is, unit, how entered, which backend field it populates, how changing it affects outputs), and every output element displayed.

### 17.1 Dashboard (`DashboardPage.jsx`)

Purpose: Starting point. Lists all projects the current user can access and provides project management actions.

Outputs shown:

Project cards: name, number of buildings, diversified demand in kVA and kW, last-modified date

Role badge per project: admin (owner), Main User, or View Only

Demand formatted via fmtVA() (VA → kVA → MVA at 1 k / 1 M thresholds) and fmtKW() (W → kW → MW)

Input actions:

| Action | Fields | Notes |
| --- | --- | --- |
| Create new project | Project name (text) | Modal with a single name field; creates an empty project |
| Edit project | Name (text) + auto-backup interval (Never / Daily / Weekly / Monthly) | Auto-backup saves a full JSON export on the chosen cadence |
| Restore from backup | JSON file (drag-and-drop or file picker) | Re-imports all buildings, floors, rooms, components, and power sources |
| Delete project | Confirmation prompt | Permanent; cannot be undone from the UI |

What the user learns here: Which projects exist, their total electrical demand, and whether they have editing rights.

### 17.2 Project Page (`ProjectPage.jsx`)

Purpose: Shows all buildings in the project, configures project-wide schedule and currency, manages team members, and accepts project-level loads.

Outputs shown:

PowerBanner (sticky top bar): diversified demand in kVA and kW, recalculated on every load change

PowerSourcesBanner: utility lines, generator lines, solar systems, and battery banks in a collapsible strip

Building cards: name, building type badge, floor count, area m²

Input actions:

| Field | Type | Unit | Backend field | Effect on output |
| --- | --- | --- | --- | --- |
| Building name | Text + autocomplete | — | buildings.name | Label only; autocomplete suggests names from existing buildings in project |
| Building type | Dropdown (12 options) | — | buildings.type | Used in building header of Electrical Design page; informs component suggestions |
| Building area | Number | m² | buildings.area_m2 | Used in solar capacity heuristic estimate |
| Currency symbol | Text (1–3 chars) | — | projects.currency_symbol | Displayed on Financial page cost figures |
| Working days | Toggle buttons Mo–Su | — | schedules.working_days | Days included in load-profile and cost calculations |
| Work hours | HH:MM–HH:MM pairs (multiple allowed) | — | schedules.work_hours | Active windows for loads with usage_day_type = weekday |
| Operating season | Month + day pairs (start date, end date) | — | schedules.operating_season | Date range for loads marked usage_season = summer or winter |

Building types: Generic, Residential House, Apartment, Hotel, Office, School, University, Retail, Hospital, Industrial, Mosque, Sports.

What the user learns here: The overall project layout and top-level demand; sets cost-accounting context via currency and schedule.

### 17.3 Building Page (`BuildingPage.jsx`)

Purpose: Shows all floors in the selected building. Accepts building-level loads (loads that belong to the whole building rather than a single floor). Same PowerBanner and PowerSourcesBanner scoped to this building.

Outputs shown:

Floor cards: name, room count, area m²

PowerBanner showing building diversified demand

Input actions:

| Field | Type | Unit | Notes |
| --- | --- | --- | --- |
| Floor name | Text | — | e.g. "Ground Floor" |
| Floor area | Number | m² | Used in area calculations and pro-rated diversity |
| Building schedule override | Same fields as project schedule | — | Overrides project schedule for this building only |

What the user learns here: How many floors the building has and how building-level demand compares to project total.

### 17.4 Floor Page (`FloorPage.jsx`)

Purpose: Lists rooms on this floor. Accepts floor-level loads. Same banner structure scoped to floor.

Outputs shown:

Room cards: name, room type badge, area m²

Input actions:

| Field | Type | Unit | Notes |
| --- | --- | --- | --- |
| Room name | Text | — | — |
| Room type | Dropdown | — | Guides component autocomplete suggestions |
| Room area | Number | m² | Used in area calculations |
| Floor schedule override | Schedule fields | — | Overrides building schedule for this floor |

What the user learns here: Demand distribution across rooms on the floor.

### 17.5 Room Page — Component Entry (`RoomPage` / `EntityComponents.jsx`)

Purpose: The primary data-entry screen. Every electrical load in the room is entered here as a component. Values entered on this screen are the source data for all outputs in the system — electrical design, load schedule, financial analysis, and phase balance all derive from these entries.

Component card (list view):

Each saved component shows: name, priority badge, flexibility badge, phase badge (1Φ / 3Φ), phase letter (A/B/C if pinned), Socket badge (if needs_socket = true), Motor badge (if is_motor = true), group name chip, VA × qty · PF value · total W, and usage time interval chips.

Component entry modal — every input field:

| Field | Type | Unit | What it is | Effect on outputs |
| --- | --- | --- | --- | --- |
| Component Name | Text + autocomplete | — | Names the component type. Autocomplete matches existing types in the project and pre-fills power/phases/PF from previous entries of the same name. Typing a new name creates a new type. | If the selected type is marked is_motor = true, triggers 125% continuous-load sizing in the Electrical Design |
| Apparent Power (VA) | Number ≥ 1 | VA | Rated apparent power of one unit. For a 36 W LED at PF=1.0 enter 36. For an AC unit with 2.5 kW real power at PF=0.85 enter 2941 VA (= 2500/0.85). Enter nameplate VA if given. | Ib = VA / 230 (1Φ) or VA / (√3 × 400) (3Φ); also P_W = VA × PF for energy calculations |
| Phases | Toggle: 1Φ / 3Φ | — | Whether the load uses one phase + neutral, or all three phases. Motors and ACs are usually 3Φ; lighting and small sockets are 1Φ. | Changes voltage divisor for Ib (230 V vs 400 V); 3Φ loads are spread equally across all three phases in the phase-balance calculation |
| Power Factor | Number 0.01–1.00 | — | Ratio of real (W) to apparent (VA) power. PF=1.0 for resistive loads (heaters, LED drivers with no reactive component). PF≈0.85 for induction motors and ACs. PF≈0.90 for switch-mode power supplies. | P_W = VA × PF; used in all energy (kWh) and cost calculations; does not affect breaker sizing (which uses VA) |
| Phase (optional, 1Φ only) | A / B / C toggle | — | Pins this load to a specific phase. If left blank, the FFD greedy algorithm assigns it automatically. | Directly determines which phase accumulates this load's VA in the phase-balance calculation |
| Number of Pieces | Integer ≥ 1 | — | Quantity of identical units in this room. Enter 6 for six identical luminaires on the same circuit. | total_VA = VA × qty; the service may combine multiple components of the same type into one circuit |
| Priority | Dropdown: Normal / Essential / Critical | — | Load priority for dispatch and protection. Selecting Critical automatically sets schedule to 24 h/day (00:00–23:59, all days, all seasons). | Critical loads → routed to ATS-backed essential panel + RCD added to circuit; Essential → preferred in source dispatch order; Normal → flexible |
| Load Scheduling Type | Dropdown: Fixed / Shiftable / Curtailable | — | How the optimizer treats this load. Fixed runs exactly at the time intervals entered below. Shiftable lets the optimizer select the cheapest window within earliest/latest bounds (no time intervals needed — optimizer assigns them). Curtailable can reduce output below rated during high-cost hours. | Only affects the "Optimized load" line on the Load Schedule page; does not change nameplate VA or breaker sizing |
| (Shiftable only) Required run hours | Integer 1–24 | h/day | How many hours per day the optimizer must guarantee this load runs | Optimizer hard constraint |
| (Shiftable only) Earliest start hour | Dropdown 00:00–23:00 | HH:00 | Earliest allowed start time | Optimizer window bound |
| (Shiftable only) Latest end hour | Dropdown 01:00–24:00 | HH:00 | Latest allowed finish time | Optimizer window bound |
| (Shiftable only) Allow split / Max interruptions | Checkbox + integer | — | Whether the optimizer may break the run into multiple sub-windows and how many times | Optimizer flexibility |
| (Curtailable only) Minimum output % | Number 1–100 | % | Floor on how much the load can be reduced (e.g. 50% means cannot curtail below half rated power) | Optimizer reduction bound |
| Usage Season | Toggle: All / Summer / Winter | — | Which seasons this load is active. "All" = year-round. Seasonal loads are excluded from energy and cost calculations during the off-season months. | Filters load from active hours in the load-profile calculation for months outside the season |
| Usage Day Type | Toggle: All / Weekday / Weekend | — | Which day types. "All" = every day. | Weekday-only loads are excluded on weekend days per the project schedule |
| Usage Time Intervals | HH:MM–HH:MM pairs, multiple allowed | — | Clock windows during which this load is on. Add multiple intervals for split-shift operation (e.g. "08:00–12:00" + "14:00–17:00"). Active hours = sum of interval durations. | kWh/day = VA × PF × Σ(interval_hours); directly sets daily energy and cost contribution |

Additional toggles (shown as badges in card view):

needs_socket = true: component requires a socket outlet on its circuit; circuit is classified as SOCKET type (adds 30 mA RCD requirement)

is_motor = true: circuit is classified HEAVY; largest-motor 125% rule applied; Curve C breaker assigned

What the user learns here: The bottom-up electrical load inventory. Every kWh and every ampere in downstream pages traces back to values entered here.

### 17.6 Load Schedule Page (`LoadSchedulePage.jsx`)

Purpose: Shows the hourly demand profile for a chosen month and day, comparing coincident peak load to the optimizer's peak-shaving result, and breaking down energy supply by source.

Controls:

| Control | Effect |
| --- | --- |
| Month picker (1–12) | Selects month for solar declination, seasonal load filtering, and NASA POWER GHI look-up |
| Day picker (day of month) | Selects the 24-hour profile day to display |

Tab 1 — Load profile:

Y-axis: kW

Max load line: coincident sum of all active loads at each hour (worst-case demand)

Optimized load line: after shiftable loads are rescheduled and curtailable loads are reduced

Reactive kVAR area: reactive power demand per hour

Tab 2 — Sources:

Solar capacity area: available solar output per hour based on irradiance model and declared system size

Utility capacity area: configured import limit per hour

Generator capacity area: rated output if a generator is configured

Tab 3 — Combined dispatch:

Stacked areas: Solar used, Battery discharge, Utility used, Generator used, Unmet demand

Battery SOC overlay line (0–100%): shows how the battery charges and drains through the day

StatCard strip (for the selected day):

Active hours (hours with non-zero demand)

kWh delivered (total energy consumed)

Source share % (what fraction came from solar / grid / generator / BESS)

Daily cost (tariff × kWh from paid sources)

What the user learns here: Whether the profile has damaging demand peaks, how much solar offsets consumption each hour, when the battery is charged or discharged, and whether any unmet demand hours exist.

### 17.7 Financial Page (`FinancialPage.jsx`)

Purpose: Shows the 25-year economic case for the configured power infrastructure versus utility-only baseline.

Controls:

Month selector (1–12): representative month used for energy-mix calculation

SummaryCard grid:

| Card | Value | What it means |
| --- | --- | --- |
| LCOE | $/kWh | Levelized cost from solar: total capital / (annual solar kWh × 25 years) |
| Payback year | Year N | Year when cumulative savings equal total capital outlay |
| Total 25-year savings | $ | Sum of utility bill reductions over project lifetime |
| Annual solar kWh | kWh | Solar energy absorbed by the building each year |
| Energy mix | % per source | Solar / Grid / Generator / BESS shares of annual consumption |

Charts:

25-year cumulative net cash flow (LineChart): runs negative initially (capital cost) then rises as savings accumulate; a ReferenceDot marks the exact payback year

Energy mix pie (PieChart): visual breakdown of annual energy by source

What the user learns here: Whether the solar/battery investment makes financial sense and the number of years to break-even.

### 17.8 Phase Balance Page (`PhaseBalancePage.jsx`)

Purpose: Shows how single-phase loads are distributed across phases A, B, C; flags imbalance; and allows manual phase reassignment.

Outputs:

PhaseBar for each phase: VA on that phase, percentage of three-phase total, line current (A = VA ÷ 230)

Phase A: indigo color

Phase B: emerald color

Phase C: amber color

Overall imbalance % and status badge: Balanced (< 10%), Warning (10–20%), Critical (> 20%)

Neutral current (A): phasor sum of three unbalanced phase currents

Current phase assignment of each room: shown as A / B / C chip or "auto"

Input actions:

PhaseAssignButtons per room: click A, B, or C to pin all 1-phase loads in that room to that phase; click Clear to return to auto-assignment

Changes take effect immediately; PhaseBar and imbalance % update in real time

What the user learns here: Whether the electrical system has an unacceptable neutral current (which causes transformer heating and potential neutral conductor overload) and which rooms to reassign to fix it.

### 17.9 Single-Line Diagram Page (`SingleLineDiagramPage.jsx`)

Purpose: Auto-generated SVG single-line schematic of the project's power topology.

Outputs:

SourceNode circles (top row, y = 60 px): one circle per configured source

Solar: yellow

BESS (battery): violet

Utility grid: blue

Generator: orange

Breaker symbol on each source-to-bus connection: small square with diagonal line

Main bus bar (horizontal line, y = 200 px, dark blue): connects all sources and feeds all buildings

BuildingNode rectangles (bottom row, y = 340 px, green): one per building, labeled with name and total kVA

Download SVG button: saves the diagram as a .svg file

SVG canvas width: 900 px; layout computed from actual source and building counts

What the user learns here: A quick visual topology check suitable for reports and presentations; confirms all sources and buildings are connected to the common bus.

### 17.10 Electrical Design Page (`ElectricalDesignPage.jsx` + `PanelScheduleTable.jsx`)

Purpose: Complete panel schedule for every floor distribution board (DB) and building main distribution board (MDB), computed from the load inventory and IEC 60364 rules.

Page-level stat cards:

| Card | Value | Notes |
| --- | --- | --- |
| Buildings | count | — |
| Floor DBs | count | Total distribution boards across all buildings |
| Total Circuits | count | Final circuits across all DBs |
| Derating Factor | 0.87 | 40 °C ambient, PVC/Cu cable, Method A1 |

Engineering notice: Cable ampacity values from IEC 60364-5-52 Table B.52.2, Method A1 (conductors in conduit in thermally insulated wall — the most conservative reference method). Enter cable run lengths in the L (m) column for live voltage-drop calculation.

Per-building section — stat cards:

| Card | Formula |
| --- | --- |
| Nameplate Total | Sum of all VA (all rooms, all components × quantity) |
| Diversified Demand | Nameplate × IEC 60364-8-1 diversity factors (room → floor → building → project) |
| MDB Incomer | Next standard MCB rating above Ib = VA_diversified / (√3 × 400) |
| Phase Imbalance % | (VA_max_phase − VA_min_phase) / VA_avg_phase × 100 |

Panel schedule table — every column:

| Column | What it shows | How computed |
| --- | --- | --- |
| # | Circuit number | Sequential within the panel |
| Type | Circuit classification badge | LIGHTING (amber), SOCKET (blue), HEAVY (red), CRITICAL (deep red), AUXILIARY (teal), MIXED (purple), FLOOR_FEEDER (indigo) — see Section 7 for classification rules |
| Phase | Phase letter A / B / C, or 3PH | From FFD greedy auto-assignment or user override on Phase Balance page |
| Rooms / Description | Room names or custom label | Rooms whose loads are grouped on this circuit |
| Loads | Component name × qty | Each load; M badge if is_motor = true |
| Total VA | Apparent power | Sum of VA × quantity for all loads on the circuit |
| Ib (A) | Design current | VA / 230 (1Φ) or VA / (√3 × 400) (3Φ); for motor circuits uses VA × 1.25 / V_nom |
| In (A) | Breaker rated current | Next standard MCB/MCCB size above Ib from IEC 60898 series: 6/10/16/20/25/32/40/50/63/80/100 A |
| Curve | Trip characteristic | B = general (lighting, resistive); C = motor loads, mixed; D = transformer inrush |
| Cable mm² | Conductor cross-section | Smallest size from IEC 60364-5-52 Table B.52.2 with derated ampacity ≥ Ib (derating = 0.87 at 40 °C) |
| PE mm² | Protective earth conductor | IEC 60364-5-54 three-band rule: cable ≤ 16 mm² → PE = cable; 16–35 mm² → PE = 16 mm²; > 35 mm² → PE = cable ÷ 2 |
| Util % | Utilisation | (Ib / In) × 100; ≤ 80% green, 80–95% amber, > 95% red |
| RCD | Residual-current device | "30 mA" badge for all SOCKET circuits and all CRITICAL-priority loads; "—" otherwise |
| L (m) | Cable run length | User-entered field; not stored server-side; session-only |
| ΔU % | Voltage drop | (mV/A/m × Ib × L) / (V_nom × 1000) × 100; limit 3% for LIGHTING, 5% for others; displayed red when exceeded with suggested next cable size |
| Note | Warnings | "⚠ Critical" if circuit contains critical-priority loads (routes to essential panel); voltage-drop note if length not yet entered |

What the user learns here: The complete switchboard design — every breaker rating and trip curve, every cable and PE size, and (after entering cable lengths) every voltage-drop value — ready for a certified panel-schedule drawing.

## Section 18 — End-to-End Worked Example

Building: Al-Noor Community School, 2 floors.

Location: Cairo area (latitude 30° N).

Project schedule: Mon–Fri, 08:00–17:00, Operating season all year.

### 18.1 Data Entry (Room Page)

Floor 1 — Ground Floor

| Room | Component | VA | PF | Qty | Phases | Priority | Season | Intervals | is_motor |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Admin Office | LED Panel | 36 | 1.00 | 2 | 1Φ | Normal | All | 08:00–17:00 | No |
| Admin Office | Office Socket | 200 | 0.90 | 4 | 1Φ | Normal | All | 08:00–17:00 | No |
| Admin Office | Ceiling Fan | 70 | 0.85 | 1 | 1Φ | Normal | All | 08:00–17:00 | No |
| Classroom 101 | LED Panel | 36 | 1.00 | 6 | 1Φ | Normal | All | 08:00–17:00 | No |
| Classroom 101 | Classroom Socket | 200 | 0.90 | 4 | 1Φ | Normal | All | 08:00–17:00 | No |
| Classroom 101 | Ceiling Fan | 70 | 0.85 | 2 | 1Φ | Normal | All | 08:00–17:00 | No |
| Classroom 101 | Split AC | 3000 | 0.85 | 1 | 3Φ | Normal | Summer | 09:00–16:00 | Yes |

Floor 2 — First Floor

| Room | Component | VA | PF | Qty | Phases | Priority | Season | Intervals | is_motor |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Server Room | LED Panel | 36 | 1.00 | 2 | 1Φ | Critical | All | auto (24 h) | No |
| Server Room | Server UPS | 1500 | 0.90 | 1 | 3Φ | Critical | All | auto (24 h) | No |
| Classroom 201 | LED Panel | 36 | 1.00 | 6 | 1Φ | Normal | All | 08:00–17:00 | No |
| Classroom 201 | Classroom Socket | 200 | 0.90 | 4 | 1Φ | Normal | All | 08:00–17:00 | No |
| Classroom 201 | Ceiling Fan | 70 | 0.85 | 2 | 1Φ | Normal | All | 08:00–17:00 | No |
| Classroom 201 | Split AC | 3000 | 0.85 | 1 | 3Φ | Normal | Summer | 09:00–16:00 | Yes |

> Selecting "Critical" priority on Server Room components automatically sets their schedule to 00:00–23:59, all days, all seasons. The user does not need to enter time intervals for Critical loads.

### 18.2 PowerBanner — Nameplate and Diversified Demand

Nameplate totals (sum of all VA × quantity):

| Level | VA |
| --- | --- |
| Admin Office | 2×36 + 4×200 + 1×70 = 942 VA |
| Classroom 101 | 6×36 + 4×200 + 2×70 + 1×3000 = 4 156 VA |
| Ground Floor | 942 + 4 156 = 5 098 VA |
| Server Room | 2×36 + 1×1 500 = 1 572 VA |
| Classroom 201 | same as 101 = 4 156 VA |
| First Floor | 1 572 + 4 156 = 5 728 VA |
| Building nameplate | 5 098 + 5 728 = 10 826 VA ≈ 10.8 kVA |

After applying IEC 60364-8-1 diversity factors at room, floor, building, and project levels (project DF = 0.70), the PowerBanner displays approximately 6.8 kVA diversified demand. The banner also shows active real power: roughly 5.9 kW (average PF ≈ 0.87).

> What the user learns: The building will realistically draw about 6.8 kVA at peak — notably less than the 10.8 kVA nameplate, because not all loads run simultaneously.

### 18.3 Electrical Design Page — MDB and Floor DBs

MDB incomer (building-level, 3-phase supply):

Ib_mdb = VA_diversified / (√3 × 400)

= 6 800 / 692.8

= 9.8 A

In_mdb = next standard size above 9.8 A → 10 A MCB, Curve B

Cable   = next size with derated ampacity ≥ 9.8 A

→ 2.5 mm² (base 17 A × 0.87 = 14.8 A derated) ✓

PE      = 2.5 mm² (cable ≤ 16 mm² → PE = cable)

Selected ground floor circuits (GF DB):

| # | Type | Phase | Description | Total VA | Ib (A) | In (A) | Curve | Cable mm² | PE mm² | Util % | RCD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| GF-01 | Lighting | A | Admin LEDs ×2 | 72 | 0.31 | 6 | B | 1.5 | 1.5 | 5% | — |
| GF-02 | Socket | A | Admin Sockets ×4 | 800 | 3.48 | 6 | B | 1.5 | 1.5 | 58% | 30mA |
| GF-03 | Lighting | B | C101 LEDs ×6 + Fans ×2 | 356 | 1.55 | 6 | B | 1.5 | 1.5 | 26% | — |
| GF-04 | Socket | B | C101 Sockets ×4 | 800 | 3.48 | 6 | B | 1.5 | 1.5 | 58% | 30mA |
| GF-05 | Heavy | 3PH | C101 AC (motor ×1.25) | 3 750 eff | 5.41 | 6 | C | 1.5 | 1.5 | 90% | — |

For circuit GF-05 (motor):

Ib_rated = 3 000 / (√3 × 400) = 4.33 A

Ib_sizing = 4.33 × 1.25 = 5.41 A   (NEC 430.24/430.22 continuous-load rule)

In        = 6 A (next standard above 5.41 A), Curve C

Util%     = 5.41 / 6 × 100 = 90%    ← amber warning; slightly oversized cable would reduce this

First floor circuits (FF DB — critical server room):

| # | Type | Phase | Description | Total VA | Ib (A) | In (A) | Curve | Cable mm² | PE mm² | Util % | RCD | Note |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| FF-01 | Critical | A | Server LEDs ×2 | 72 | 0.31 | 6 | B | 1.5 | 1.5 | 5% | 30mA | ⚠ Critical |
| FF-02 | Critical | 3PH | Server UPS ×1 | 1 500 | 2.17 | 6 | B | 1.5 | 1.5 | 36% | 30mA | ⚠ Critical |

The page also shows an Essential Panel Required notice: critical-priority circuits must be supplied from an ATS-backed essential busbar.

Voltage drop check (GF-02, socket circuit, cable run L = 25 m):

mV/A/m for 1.5 mm² ≈ 24 mV/A/m

ΔU (V)  = 24 × 3.48 × 25 / 1000 = 2.09 V

ΔU (%)  = 2.09 / 230 × 100     = 0.91%   (limit 5% → OK)

> What the user learns: Complete switchboard design in one view — every breaker, every cable, every PE conductor. The motor circuit's 90% utilisation is an amber flag; the user knows to consider a larger cable on that run.

### 18.4 Phase Balance Page

Auto-assignment result (FFD greedy algorithm):

| Phase | 1Φ loads | 3Φ share | Total VA | Current (A) |
| --- | --- | --- | --- | --- |
| A | Admin office loads = 1 082 VA | 2 500 VA | 3 582 VA | 15.6 A |
| B | C101 LEDs + fans = 356 VA; C201 LEDs + fans = 356 VA = 712 VA | 2 500 VA | 3 212 VA | 14.0 A |
| C | C101 sockets = 800 VA; C201 sockets = 800 VA = 1 600 VA | 2 500 VA | 4 100 VA | 17.8 A |

VA_avg        = (3 582 + 3 212 + 4 100) / 3 = 3 631 VA

Imbalance %   = (4 100 − 3 212) / 3 631 × 100 = 24.5%   → CRITICAL badge (red)

Neutral current:

I_N = √(15.6² + 14.0² + 17.8² − 15.6×14.0 − 14.0×17.8 − 17.8×15.6)

= √(243.4 + 196.0 + 316.8 − 218.4 − 249.2 − 277.7)

= √(756.2 − 745.3)

= √10.9 ≈ 3.3 A

After manual reassignment (user assigns Classroom 201 sockets to Phase A, Server LEDs to Phase A):

Phase A: 1 082 + 72 (server LEDs) + 800 (C201 sockets) = 1 954 VA → 4 454 VA total

Phase B: 712 + 800 (C101 sockets) = 1 512 VA → 4 012 VA total

Phase C: 800 remaining VA → 3 300 VA total

After second adjustment (split C101 fans to Phase C):

Best achievable with this load set ≈ 5% imbalance → Balanced badge

> What the user learns: The auto-assigned layout was critically unbalanced because the socket loads all fell on Phase C. Manual reassignment distributes the load and reduces the neutral current from 3.3 A to below 0.5 A.

### 18.5 Load Schedule Page (August, peak summer day)

Daily energy calculation for all loads (August working day, 08:00–17:00 school day):

| Load | W (= VA × PF) | Active hours | kWh/day |
| --- | --- | --- | --- |
| Admin LEDs ×2 | 72 W | 9 | 0.65 |
| Admin Sockets ×4 | 720 W | 9 | 6.48 |
| Admin Fan ×1 | 59.5 W | 9 | 0.54 |
| C101 LEDs ×6 | 216 W | 9 | 1.94 |
| C101 Sockets ×4 | 720 W | 9 | 6.48 |
| C101 Fans ×2 | 119 W | 9 | 1.07 |
| C101 AC ×1 (summer) | 2 550 W | 7 (09–16) | 17.85 |
| C201 LEDs ×6 | 216 W | 9 | 1.94 |
| C201 Sockets ×4 | 720 W | 9 | 6.48 |
| C201 Fans ×2 | 119 W | 9 | 1.07 |
| C201 AC ×1 (summer) | 2 550 W | 7 (09–16) | 17.85 |
| Server LEDs ×2 | 72 W | 24 | 1.73 |
| Server UPS ×1 | 1 350 W | 24 | 32.40 |
| Total |  |  | 96.5 kWh/day |

Peak coincident demand (09:00–16:00 when ACs are also running):

P_peak = 72 + 720 + 59.5 + 216 + 720 + 119 + 2 550 + 216 + 720 + 119 + 2 550 + 72 + 1 350

= 9 484 W ≈ 9.5 kW

Solar declination for August 15 (DOY = 227):

δ = 23.45 × sin(360/365 × (227 − 81))

= 23.45 × sin(144.0°)

= 23.45 × 0.588

= 13.8°

Solar capacity (1 solar system configured, area = 50 m²):

P_solar = 50 × 0.17 × 1000 × 0.75 = 6 375 W ≈ 6.4 kW

With PSH ≈ 6.5 h/day in Cairo in August:

Daily solar energy = 6.4 × 6.5 = 41.6 kWh/day

The Load Schedule combined-dispatch tab shows solar covering the daytime load from roughly 07:00–17:00; server load at night draws entirely from utility.

> What the user learns: The two ACs account for 37% of daily energy (35.7/96.5). Solar with 50 m² covers about 43% of daily demand. The server is the dominant overnight load.

### 18.6 Financial Page

Monthly energy (22 working days + 8 non-working server-only days):

Monthly kWh = 62.4 kWh/workday × 22 + 34.1 kWh/non-workday × 8

≈ 1 373 + 273 = 1 646 kWh/month     (in August)

(62.4 = 96.5 − 34.1 server portion; 34.1 = server loads × 24 h)

Solar generated (August):

Monthly solar = 41.6 kWh/day × 30 = 1 248 kWh

Solar covers: 1 248 / 1 646 = 75.8% of August demand.

Remaining from utility: 1 646 − 1 248 = 398 kWh.

At tariff $0.05/kWh: utility cost = $19.90/month.

Without solar: 1 646 × $0.05 = $82.30/month.

Monthly saving: $62.40.

LCOE and payback (capital = 6.4 kW × $800/kW = $5 120):

Annual solar kWh used ≈ 1 248 × 12 = 14 976 kWh

LCOE = $5 120 / (14 976 kWh × 25 years) = $0.0136/kWh

Annual saving ≈ $62.40 × 12 = $748.80

Payback year = $5 120 / $748.80 ≈ 6.8 → Year 7

25-year total saving = $748.80 × 25 − $5 120 = $13 600

> What the user learns: A 6.4 kW system pays back in about 7 years and saves roughly $13 600 over 25 years. LCOE of $0.014/kWh is far below the $0.05/kWh tariff.

### 18.7 Single-Line Diagram

For this project (1 utility line + 1 solar system + no battery + no generator), the SVG shows:

Source row (y = 60): Grid circle (blue) · Solar circle (yellow)

Breaker symbols on both source connections

Bus bar (y = 200): horizontal dark-blue line

Building row (y = 340): "Al-Noor School" rectangle labeled "6.8 kVA"

> What the user learns: Topology confirmed — two sources feed one common bus which supplies one building. Suitable for attaching to a permit application.

## Section 19 — Glossary

Apparent power (VA, kVA): The product of voltage and current without regard to phase angle. For a single-phase 230 V circuit drawing 10 A, apparent power = 2 300 VA = 2.3 kVA. Electrical equipment is rated in VA because conductors and transformers must carry the full current regardless of power factor.

Real (active) power (W, kW): The power actually converted to useful work (heat, light, mechanical). P (W) = VA × power factor. A 2 300 VA load at PF = 0.87 delivers 2 001 W of real power.

Reactive power (VAR, kVAR): Power stored and returned by inductors and capacitors each cycle. Does no useful work but flows through conductors and causes losses. Q (VAR) = √(VA² − W²).

Power factor (PF): Ratio of real to apparent power: PF = W / VA = cos φ. PF = 1.0 for purely resistive loads (heaters, incandescent lamps). PF ≈ 0.85 for induction motors and ACs. PF ≈ 0.90 for switch-mode power supplies. Low PF means higher current for the same real power, requiring larger conductors.

Diversity factor (DF) / Coincidence factor: The ratio of maximum coincident demand to the sum of individual maximum demands. A DF of 0.70 means the actual peak is 70% of the nameplate total because not all loads are on simultaneously. IEC 60364-8-1 defines diversity factors for different occupancy types. The inverse of coincidence factor is sometimes called demand factor.

Coincident demand (nameplate total): The hypothetical load if every component ran at its full rated VA at the same instant. This is the worst case; used for breaker sizing at each level.

Diversified demand: Nameplate demand scaled by diversity factors. This is what the supply transformer and incomer must actually handle.

Ampacity: The maximum continuous current a conductor can carry without exceeding its rated temperature. IEC 60364-5-52 Table B.52.2 tabulates base ampacities for PVC/Cu cables by cross-section and installation method. Method A1 (in conduit in insulated wall) gives the most conservative values.

Derating: Reducing rated ampacity to account for elevated ambient temperature or cable grouping. At 40 °C, a 0.87 derating factor is applied to the IEC Table B.52.2 base values (which are for 30 °C). Example: 2.5 mm² base ampacity 17 A × 0.87 = 14.8 A derated.

RCD (Residual-Current Device) / RCCB: A protective device that trips when the difference between live-conductor current and neutral-conductor current exceeds a threshold — indicating current leaking to earth through a fault or a person. A 30 mA RCD trips in ≤ 40 ms, which is below the let-through current needed to cause cardiac fibrillation. Required on socket circuits (IEC 60364) and on critical-priority circuits in this system.

MCB (Miniature Circuit Breaker): A resettable protective device rated up to 125 A (IEC 60898) that breaks the circuit on overload (thermal trip) or short circuit (magnetic trip). Ratings in this system follow the standard IEC series: 6/10/16/20/25/32/40/50/63/80/100 A.

MCCB (Moulded Case Circuit Breaker): Larger version of the MCB, typically 100–3 000 A, used as building incomers or large motor feeders (IEC 60947-2).

Trip curve B: MCB magnetic trip at 3–5× In. For resistive loads and lighting circuits where there is no startup inrush.

Trip curve C: Magnetic trip at 5–10× In. For loads with moderate inrush — motors, fluorescent luminaires, small transformers.

Trip curve D: Magnetic trip at 10–20× In. For high-inrush loads such as large transformer primaries, solenoids, and welding equipment.

DB (Distribution Board): The sub-panel on each floor that receives the floor feeder from the MDB and distributes power to final circuits in rooms on that floor. In this system, each floor has one DB.

MDB (Main Distribution Board): The primary panel in each building. Receives the utility supply (or generator/ATS output) and feeds floor DBs and any building-level circuits.

PE (Protective Earth conductor): The green/yellow conductor connecting exposed conductive parts of equipment to the earthing system. Sized per IEC 60364-5-54: for cables ≤ 16 mm² the PE equals the phase conductor; for 16–35 mm² the PE is fixed at 16 mm²; for > 35 mm² the PE is half the phase conductor area.

PSH (Peak Sun Hours): The number of hours per day during which solar irradiance equals 1 000 W/m² (STC — Standard Test Conditions). A location with PSH = 6 will receive the same daily energy as 6 hours of full-sun irradiance. PSH is used to estimate daily solar output: E_day = P_stc × PSH.

GHI (Global Horizontal Irradiance): Total solar energy (direct + diffuse) incident on a horizontal surface per unit area per day, measured in Wh/m² or kWh/m²/day. This system retrieves GHI from the NASA POWER API for the project's latitude/longitude.

SOC (State of Charge): Battery energy level expressed as a percentage of rated capacity (0% = empty, 100% = full). The dispatch logic prevents charging above soc_max (typically 95%) and discharging below soc_min (typically 10–20%) to protect battery longevity.

RTE (Round-Trip Efficiency): The fraction of energy returned by a battery compared to the energy put in during charging. A battery with RTE = 0.90 returns 90 Wh for every 100 Wh charged. In the system, one_way_efficiency = √(RTE), applied once on charge and once on discharge so the combined effect equals RTE.

LCOE (Levelized Cost of Electricity): Total lifetime cost of a generation asset divided by total lifetime energy produced. LCOE = Capital_cost / (Annual_kWh × Lifetime_years). This system uses a simple undiscounted form over 25 years; it does not apply NPV or IRR.

Utilisation percentage (Util %): The ratio of design current to breaker rated current: Util% = (Ib / In) × 100. Values below 80% are green (adequate headroom), 80–95% amber (acceptable but limited), above 95% red (overcrowded — consider the next cable/breaker size up).

Phase imbalance %: (VA_max_phase − VA_min_phase) / VA_avg_phase × 100. Measures how unevenly single-phase loads are distributed across the three phases. IEC guidelines suggest < 10% as balanced; 10–20% is a warning; > 20% is unacceptable because it causes thermal stress in transformers, excess neutral current, and voltage asymmetry. The system uses: Balanced < 10%, Warning 10–20%, Critical > 20%.

Neutral current: In a balanced three-phase system the neutral carries zero current because the three phasor currents cancel. As loads become unbalanced, residual current flows in the neutral: I_N = √(I_A² + I_B² + I_C² − I_A·I_B − I_B·I_C − I_C·I_A). Excessive neutral current overheats the neutral conductor (which is not protected by a breaker in most installations) and increases transformer losses.